## Sheet1
| www.ihiconnectors.com |  |  | www.LugsDirect.com
HEAT LOSS in WATTS of connectors and conductors in a stable temperature environment without fan cooling
CONVECTION THEORY (Surface to Air only) | [6 empty] | Qc = h. Ac. (T - Ta)
VARIABLE |  | UNITS | Fill in blue fields only
Qc | 0.50216 | Watts | Watts transferred from cooling surface by convection
Ac | 0.00078 | M2 | 1.2108 | in2 | Ac = Area of the complete cooling surface contacted by air including fins
which are not excessively tall, say ratios (say< 2:1)
h | 8.9416 | W/M2 oK | h = Heat Transfer Coefficient for configuration ( a constant per degree for convection)
Horizontal/Vertical metal surfaces = typ. range 8.07 - 9.05 Watts/M2-K with no radiation component
After 800 deg F linearity rolls off perhaps due to radiation leaks in idealized rig
T | 365 | oK | 92 | oC | 197.6 | oF | T = Temp of surface
Ta | 293 | oK | 20 | oC | 68 | oF | Ta = Temp of ambient surroundings
0.0032 | W/in2-oF | 8.9416 |  |  | W/(M2 oK) | About .00288 - .00324 Watts/inch2/ deg F slope from charts below
RADIATION THEORY ( Surface to space only) | [6 empty] | Qr = e * Sigma *Ar * ( T4 - Ta4 )
Qr | 0.045902 | Watts | Qr = Watts transferred from cooling surface by radiation
Ar | 0.00078 |  | 1.2108 | in2 | Ar = Area of envelope of surface (## see below)
Sigma | 5.67e-08 | W/M2 oK4 | Sigma = Stefan-Boltzman constant |  |  |  | Offset by adding back the incoming radiation from
T | 365 | oK | T = Temp of radiating surface |  |  |  | surroundings (at room temp radiation loss/gain = 0)
Ta | 293 |  | Ta = Temp of ambient area (for incoming radiation offset only)
e | 0.1 |  | e = Emissivity | Mirror = 0, Lamp black = 1. Shiny alum 0.1, Shiny Tin Plating .07, copper oxid'd 0.7-0.8
Copper shiny .08, galv (zinc plate) 0.28, Lead shiny 0.08, lead oxidised 0.63, steel rolled .24
Total, Qt | 0.54806 | Watts | ## Do not count "fin" area of re-entrant shapes.Radiation area is radial ENVELOPE, NOT total
surface area, due to mutual radiation re-absorbtion in slots, threads and holes.
Two graphs below do not correspond to the 70F zero heat loss point but do give a good average of around .003 watts/in2 per delta degree F
Slope = | 0.002887 | watts/in2 per delta F |  |  |  | source of chart | www.watlow.com
70 | 0
155 | 0.1
180 | 0.2
230 | 0.3
265 | 0.4
335 | 0.6
400 | 0.8
475 | 1
810 | 2
slope = | 0.00324 | watts/in2 per delta F |  |  |  | source of chart | www.watlow.com
500 | 1.4
800 | 2.4
1300 | 4
Watts Created = I2R |  |  | Alloy Name | Leaded gunmetal Bronze C836 dual #10 out tap
Test amps from Heat Cycling chart UL 486 |  |  |  | 75
Cross section of connector |  |  |  | 1.8e-05 | m2 | 0.027942 | in2 | 0.18 | cm2 | 0.18861 | in (round dia equiv)
Length of connector |  |  |  | 1.25 | cm | 0.49213 | in | 0.0125 | M | 4.101e-05 | Thousand feet
Resistivity of material |  |  |  | 11.49 | ΩMx10-8 | 11.49 | μΩcm
Resistance over length and cross section (calc) |  |  |  | 7.9792e-05 | Ω
Physical measured resistance (REF) |  |  |  | 8e-06 | Ω | 0.045 | W
Physical measured voltage drop (REF) |  |  |  | 0.006 | V | 0.45 | W
WATTS created by connector resistance (calc) |  |  |  | 0.44883 | W
COMPARE TO PREDICTED WATTS |  |  |  | 1.2211 | Meets requirement by |  | 22.11%
Resistivities
Copper 110 | 1.78 - 1.67 | ΩMx10-8
Brass 360 | 6.6 - 6.2 | ΩMx10-8
Brass Red | 4.7 | ΩMx10-8 |  | © This calculator method, spreadsheet and fomat copyright of Charles D M Ridley 2003-2007. cridley@ihinet.com
|  | ΩMx10-8 |  | All publishing rights reserved. Granted unlimited personal use but solely at your own risk
Bronze 554 | 9.1 | ΩMx10-8 |  | No claims are made as to the accuracy and fitness for any particular use.
Bronze 836 | 11.49 | ΩMx10-8 |  | Use only for cross checks before actual testing and final design. Bad data in = bad results out
Alum 6061-T6 | 4.07 | ΩMx10-8 |  | Copy and print only the entire document
Alum 6101-T6 |  | ΩMx10-8 |  | Thanks and acknowledgements to Witlow for convection charts
Alum 2024-T4 | 5.8 | ΩMx10-8
Alum 2024-T6 |  | ΩMx10-8
Alum 2011-T3 | 4.8 | ΩMx10-8
Alum 6062-T6 | 3.7 | ΩMx10-8
ΩMx10-8
ΩMx10-8
Hi alloy Steel | 59 - 75 | ΩMx10-8
Lo alloy steel | 16 - 9.6 | ΩMx10-8
Gold | 2.4 | ΩMx10-8
Silver | 1.6 | ΩMx10-8
Temperature Calculation Chart Degrees Fahrenheit to 5 Degrees Celcius ---------> C = ---(F-32) 9 Degrees Kelvin to Degrees Celcius ------------> C = K-273.15 Degrees Celcius to 9 Degrees Fahrenheit ---------> F = ---C + 32 5